# PRODUCT SPECIFICATION

- PRODUCT CODE HMC02/1.5

- DESCRIPTION	2 Core 30/.25 (1.5mmsq). T.C.W. V90HT PVC insulated. White cores numbered V90HT P.V.C. sheathed.

Control cable. 450/750 volt to AS5000.3 Oxygen Free copper. RoHS compliant PVC.

# CONSTRUCTION

  - CONDUCTOR : 30 strands of 0.25 mm nom. Tinned Annealed Copper to

AS1125 drawn from Class 102 copper to AS1574.

Max. D.C. resistance at 20C : 13.3 ohms / km

  - INSULATION : White V90HT PVC to AS3808.

Nominal  Diameter:	2.7 mm Nominal Wall Thickness: 0.6 mm

  - LAY  UP	2 Cores laid up

1. White  No1	2. White  No2

  - SHEATH	Coloured P.V.C. type V90HT  to AS3808.

Nominal  Diameter:	7.9 mm Nominal Wall Thickness:    1.2 mm

# IDENTIFICATION

Printed on sheath at approx. 500mm intervals

TYCAB 2 X 1.5MMSQ 2019 V90HT ELECTRIC CABLE 450/750V